# 3-Pump 3-Tank Backup System

Program Documentation

# 1. Overview

This PLC program controls a water distribution system with 3 pumps and 3 tanks. Each pump is dedicated to filling one tank, but the system includes backup logic so that if a pump fails, a neighboring pump can take over and fill the affected tank through interconnecting valves.

| Controller | Schneider Electric TM221CE24T (Modicon M221) |
| --- | --- |
| Software | EcoStruxure Machine Expert - Basic |
| File | Pump_Tank_TM221.smbp |

# 2. System Architecture

WATER SOURCE
                             |
             +---------------+---------------+
             |               |               |
         [PUMP 1]        [PUMP 2]        [PUMP 3]
             |               |               |
             v               v               v
         +-------+       +-------+       +-------+
         |       |       |       |       |       |
         |TANK 1 |<----->|TANK 2 |<----->|TANK 3 |
         |       |VALVE12|       |VALVE23|       |
         +-------+       +-------+       +-------+

## Normal Operation

Pump 1 fills Tank 1

Pump 2 fills Tank 2

Pump 3 fills Tank 3

Valves between tanks remain CLOSED

## Backup Operation

If Pump 1 fails: Pump 2 takes over Tank 1, Valve 1-2 OPENS

If Pump 2 fails: Pump 3 takes over Tank 2, Valve 2-3 OPENS

# 3. I/O Assignment

## Digital Inputs (12 of 14 used)

| Address | Symbol | Description | Type |
| --- | --- | --- | --- |
| %I0.0 | START_BTN | System Start Button | NO |
| %I0.1 | STOP_BTN | System Stop Button | NC |
| %I0.2 | PUMP1_SPEED_OK | Pump 1 Zero Speed Sensor | NC |
| %I0.3 | PUMP2_SPEED_OK | Pump 2 Zero Speed Sensor | NC |
| %I0.4 | PUMP3_SPEED_OK | Pump 3 Zero Speed Sensor | NC |
| %I0.5 | TANK1_LOW | Tank 1 Low Level Switch | NO |
| %I0.6 | TANK1_HIGH | Tank 1 High Level Switch | NO |
| %I0.7 | TANK2_LOW | Tank 2 Low Level Switch | NO |
| %I0.8 | TANK2_HIGH | Tank 2 High Level Switch | NO |
| %I0.9 | TANK3_LOW | Tank 3 Low Level Switch | NO |
| %I0.10 | TANK3_HIGH | Tank 3 High Level Switch | NO |
| %I0.11 | FAULT_RESET | Fault Reset Button | NO |

Note: Zero speed sensors are wired NC (Normally Closed). When the motor is running at speed, the contact is CLOSED (signal = 1). When motor stops or fails, contact OPENS (signal = 0).

## Digital Outputs (10 of 10 used)

| Address | Symbol | Description | Load Type |
| --- | --- | --- | --- |
| %Q0.0 | PUMP1_RUN | Pump 1 Motor Contactor | Relay/24VDC |
| %Q0.1 | PUMP2_RUN | Pump 2 Motor Contactor | Relay/24VDC |
| %Q0.2 | PUMP3_RUN | Pump 3 Motor Contactor | Relay/24VDC |
| %Q0.3 | VALVE_12 | Valve between Tank 1-2 | Solenoid |
| %Q0.4 | VALVE_23 | Valve between Tank 2-3 | Solenoid |
| %Q0.5 | PUMP1_FAULT_IND | Pump 1 Fault Indicator | Lamp |
| %Q0.6 | PUMP2_FAULT_IND | Pump 2 Fault Indicator | Lamp |
| %Q0.7 | PUMP3_FAULT_IND | Pump 3 Fault Indicator | Lamp |
| %Q0.8 | SYSTEM_RUN_IND | System Running Indicator | Lamp |
| %Q0.9 | ALARM_OUTPUT | Alarm Horn/Buzzer | Horn |

## Memory Bits

| Address | Symbol | Description |
| --- | --- | --- |
| %M0 | SYSTEM_RUN | System Running Status |
| %M1 | PUMP1_CMD | Pump 1 Fill Command |
| %M2 | PUMP2_CMD | Pump 2 Fill Command |
| %M3 | PUMP3_CMD | Pump 3 Fill Command |
| %M10 | PUMP1_FAULT | Pump 1 Fault Latch |
| %M11 | PUMP2_FAULT | Pump 2 Fault Latch |
| %M12 | PUMP3_FAULT | Pump 3 Fault Latch |
| %M20 | TANK1_BACKUP | Tank 1 Needs Backup (Pump 2) |
| %M21 | TANK2_BACKUP | Tank 2 Needs Backup (Pump 3) |

## Timers

| Address | Symbol | Type | Time Base | Preset | Description |
| --- | --- | --- | --- | --- | --- |
| %TM0 | PUMP1_DELAY | TON | 1 second | 2 | Pump 1 startup delay |
| %TM1 | PUMP2_DELAY | TON | 1 second | 2 | Pump 2 startup delay |
| %TM2 | PUMP3_DELAY | TON | 1 second | 2 | Pump 3 startup delay |

# 4. Program Logic (19 Rungs)

## Rung 1: System Start/Stop Control

START_BTN        STOP_BTN(NC)
--+----[/I0.0]----+----[/I0.1]-------------------(M0)---
  |               |                              SYSTEM_RUN
  +----[/M0]------+
      SEAL-IN

Logic:

Press START button to energize SYSTEM_RUN

SYSTEM_RUN seals in (latches) through parallel contact

Press STOP button (NC) to de-energize and stop system

## Rungs 2-4: Pump Command Logic

Each pump command follows this pattern:

SYSTEM_RUN    TANK_LOW     TANK_HIGH(NC)  PUMP_FAULT(NC)
----[/M0]-------[/I0.x]-------[/I0.y]--------[/M1x]-------(Mx)---
                                                          PUMP_CMD

Conditions for pump to command ON:

System must be running (%M0 = 1)

Tank low level switch active (tank needs water)

Tank high level switch NOT active (tank not full)

No fault on this pump

## Rungs 6, 8, 10: Zero Speed Fault Detection

TIMER.Q       SPEED_OK(NC)   FAULT_RESET(NC)
--+---[/TMx.Q]-----[/I0.x]---+----[/I0.11]------------(M1x)---
  |                          |                        PUMP_FAULT
  +--------[/M1x]------------+
           LATCH

Fault Detection Logic:

After timer expires (pump has had 2 seconds to reach speed)

If SPEED_OK signal is FALSE (motor not spinning)

Then FAULT is SET and LATCHED

Fault remains latched until FAULT_RESET button is pressed

Why 2-second delay? Motors need time to accelerate. The delay prevents false fault detection during startup.

## Rungs 11-12: Backup Request Logic

Tank 1 Backup (Rung 11):

PUMP1_FAULT   TANK1_LOW    PUMP2_FAULT(NC)
----[/M10]-------[/I0.5]-------[/M11]-------------------(M20)---
                                                      TANK1_BACKUP

If Pump 1 has faulted AND Tank 1 needs water AND Pump 2 is healthy, request backup.

Tank 2 Backup (Rung 12):

PUMP2_FAULT   TANK2_LOW    PUMP3_FAULT(NC)
----[/M11]-------[/I0.7]-------[/M12]-------------------(M21)---
                                                      TANK2_BACKUP

If Pump 2 has faulted AND Tank 2 needs water AND Pump 3 is healthy, request backup.

## Rungs 13-14: Valve Control

Valves open automatically when backup mode is active, allowing the backup pump to fill the affected tank through the interconnection.

TANK1_BACKUP (%M20) -> VALVE_12 (%Q0.3)

TANK2_BACKUP (%M21) -> VALVE_23 (%Q0.4)

## Rungs 15-19: Indicators and Alarm

Rung 15: PUMP1_FAULT (%M10) -> PUMP1_FAULT_IND (%Q0.5)

Rung 16: PUMP2_FAULT (%M11) -> PUMP2_FAULT_IND (%Q0.6)

Rung 17: PUMP3_FAULT (%M12) -> PUMP3_FAULT_IND (%Q0.7)

Rung 18: SYSTEM_RUN (%M0) -> SYSTEM_RUN_IND (%Q0.8)

Rung 19: Any Fault -> ALARM_OUTPUT (%Q0.9)

# 5. Operating Procedures

## System Startup

Verify all tanks have correct level sensor readings

Verify all pumps are ready (no mechanical issues)

Verify zero speed sensors are functional

Press START button

System Running indicator illuminates

Pumps will automatically start filling low tanks

## Fault Handling

When a pump fault occurs:

Fault indicator lamp illuminates

Alarm sounds

Backup pump (if available) takes over

Interconnecting valve opens

To clear a fault:

Fix the mechanical issue with the pump

Verify motor can spin freely

Press FAULT_RESET button

Fault indicator extinguishes

Normal operation resumes

## System Shutdown

Press STOP button

All pumps stop immediately

All valves close

System Running indicator extinguishes

# 6. Troubleshooting

| Symptom | Possible Cause | Solution |
| --- | --- | --- |
| Pump won't start | Tank high level active | Check level sensors |
| Pump won't start | Pump fault latched | Reset fault, check motor |
| False fault alarm | Zero speed sensor failed | Replace sensor |
| False fault alarm | Timer too short | Increase preset (currently 2s) |
| Backup not working | Backup pump also faulted | Repair backup pump |
| Valve stuck closed | Solenoid failed | Check solenoid coil |

# 7. Maintenance Schedule

| Task | Frequency |
| --- | --- |
| Test START/STOP buttons | Weekly |
| Test FAULT_RESET button | Weekly |
| Verify level sensor operation | Monthly |
| Test zero speed sensors | Monthly |
| Full system test (simulate faults) | Quarterly |

# 8. Document Information

| Program Version | 1.0 |
| --- | --- |
| Created | December 2024 |
| Controller | TM221CE24T |
| Total Rungs | 19 |
| Inputs Used | 12 of 14 |
| Outputs Used | 10 of 10 |
| Timers Used | 3 |